ANEXA 5   Gas quality specifications (valid for deliveries from Romania to the Republic of Moldova and from the Republic of Moldova to Romania, under reference conditions 25ºC/0ºC)

Chemical compositions (in mole percent)

Methane (C1)						minimum  85

Ethane (C2)						maximum  10

Propane (C3)						maximum  3.5

Butane (C4)						maximum  1.5

Pentane (C5)						maximum  0.5

Hexane+(C6+)						maximum 0.2

Nitrogen (N2)						maximum 10

Carbon dioxide (CO2)					maximum 8

Oxygen (O2)						maximum 0.02

Sulphur content

Hydrogen sulphide (H2S)				maximum 6.8 mg/m3

Mercaptan sulphur (C2H5SH)				maximum 8 mg/m3

Total Sulphur                                                                 maximum 100 mg/m3

Gross Calorific Value                                                   minimum 9.612 kWh/m3

Hydrocarbon Dew Point

No hydrocarbons shall condensate at a temperature of zero degrees Celsius (O°C) at the delivery pressure.

Water dew point

Not higher than minus 8 degrees Celsius (-8⁰ C) at a pressure of 39.2 barg.

Impurities

Content of mechanical impurities: max. 0.05 mg/ m3

Temperature

maximum plus 50 ˚C